DAILY FIELD REPORT - 2026-04-25

Project: Morena Conveyance North

Resident Engineer: Terry West

Weather: , Cloudy

Hours: 07:00 - 15:30

General Notes:

Marian Bear Park spread base to work towards final grade, ran out of base well before achieving final grade .@ Rose Canyon they are continuing to weld the 30" and 42" connection spools in the shaft. @ Executive they are pushing more water into the 48" to get to 225 psi.

Activities Detail

----------------------------------------

Marian Bear Park - OHLA - Vault Work and Grading

• Spread base material that was delivered last week.

• The quantity of base was insufficient to make final grade; however, the vault and valve cans were able to get covered and near finish grade

• At 9:00 AM, the crew shifted to working inside the vault.

• Installed valve handle extensions inside the vault.

• Yesterday redhead anchors were installed underneath the flange supports for the drain line, today they reinstalled the plug valves and pipe spool/GE coupling that were removed for the anchor install. Note - the flange supports sit approx. 6" above the ground, without taller supports or pouring a pedestal, about 6" of grout would be needed under the support while the drawings call for max of 3". I explained this to the contractor so they know ahead of time. This will be a bigger issue at BO 6 and 7 as the distance from the bottom of the flanges support goes up into the 1-2' distance.

• They planned to install the drain tap and run it over to the vault drain basin but they opted to grout the interior joints of the vault and the valve handle extension penetrations instead.

Manpower:

LL-03- Laborers - QTY 4 - 8 HRS EA - OHL NA

LL-02- Foreman - QTY 2 - 8 HRS EA - OHL NA

Equipment:

LE-42- Utility Truck - QTY 1 - 8 HRS EA - OHL NA

LE-70- Generator - QTY 1 - 8 HRS EA - OHL NA

Executive - OHLA - Hydrostatic Testing

• Monitored and filled the 48-inch line for a hydro test.

• The line was left at 160 PSI last night.

• Crew continued filling the pipeline for the hydrostatic test.

• A leak emerged at the dish head weld when the pressure reached approximately 170-180 PSI.

• The repair will require the crew to de-pressurize and dewater the line to lower the water level below the weld.

• This issue is expected to cause a one to two-week schedule delay.

Manpower:

LL-03- Laborers - QTY 2 - 4 HRS EA - OHLA

Equipment:

Rose Canyon - OHLA - Phase 2 to 3 connection

• OHLA is back at rose canyon to finish the connection between phase 2 and 3, 4 laborers, 2 welders, 1 CWI were on site, the railway flagger was no longer needed as the crane would not be running any more for this operation.

• With the 42in and 30in place as of the end of day yesterday, both lines were partially welded, since the inside of the pipe was not accessible due to lack of means for safe entry and lack of air flow only the outer welds were welded per AWWA 207, which allows for outer welds only when closure joints make inner welds not possible.

• The welders came in and finished out the butt strap welds on the vertical and horizontal sections of the connection spools

• Finished welding at 12:30 rolled up and left the area. other work was planned, importing base to the site, connecting the 4" fiber optic conduit, and demobilizing equipment from the site; however, due to changes and lack of the GF and foreman onsite the remaining work was pushed till Monday

Manpower:

LL-03- Laborers - QTY 2 - 8 HRS EA - OHLA

LL-20- Certified Welding Inspector (CWI) - QTY 1 - 7 HRS EA - IQC Infrastructure

LL-19- Welder - QTY 2 - 7 HRS EA - Deans Welding

Equipment:

LE-58- Welding Truck - QTY 1 - 0 HRS EA – Deans Welding

LE-51- Pickup Truck - QTY 1 - 0 HRS EA - OHLA

LE-32- Skytrak Forklift - QTY 1 - 0 HRS EA - OHLA

LE-28- Water Truck - QTY 1 - 0 HRS EA - OHLA